## Sheet1
mixed waste | 80 | % | [5 empty] | Cost of HFO | 500 | €/t
HFO | 20 | % | [5 empty] | Cost of mixed-waste | 8.6 | €/t | density of mixed-waste | 430 | kg/m3 | 20 | €/m3
Electricity Production | 450000 | MWh/a | 1 | MWh | 3600 | MJ
Annual Operational Period | 7000 | h/a | 1 | t | 1000 | kg |  | anual HFO cost | 39901477.8325
Electricity Efficiency | 40 | % | [5 empty] | annual mixed-waste Cost | 1466526.3158
Heat Efficiency | 50 | % | [6 empty] | 41368004.1483
Calorific Value HFO | 40.6 | MJ/kg | 11.2778 | MWh/t
Calorific Value mixed-waste | 19 | MJ/kg | 5.2778 | MWh/t |  |  |  | cost of cofiring biomass boiler | 4000 | €/kWfuel
[8 empty] | cost of boiler | 257142857.1429
Electric power |  | 64.2857 | MWe |  |  |  |  | single fuel boiler cost reduction | 6000 | 20000 | €/MWe
Thermal Power |  | 80.3571 | MWth | [5 empty] | 385714.2857 | 1285714.2857
Fuel Power |  | 160.7143 | MWfuel
Sox Contol
Total energy from fuel | 1125000 | MWh/a | [5 empty] | life span | 70 | years
Heat energy | 562500 | MWh/a | [5 empty] | interest rate | 5%
[9 empty] | upper | lower | avg
Energy produced from waste |  | 900000 | MWh/a |  |  |  |  | installation cost rate | 35 | 57 | 46 | €/kWfuel | annuity
Energy produced using HFO |  | 225000 | MWh/a |  |  |  |  | installation cost | 39375000 | 64125000 | 51750000 |  | 0.051699
[8 empty] | annual operation cost rate | 0.2 | 0.8 | 0.5 | €/MWhfuel
Mass of mixed waste processed | t/a | 170526.3158 | [5 empty] | annual operation cost | 225000 | 900000 | 562500
mass of HFO needed | t/a | 79802.9557 | [5 empty] | Cost per year |  |  | 3237931.1691
mass of total fuel | t/a | 250329.2715
mass % of HFO | % | 31.8792 | [5 empty] | Nox Control
mass% of mixed-waste | % | 68.1208 | [5 empty] | lifespan
[9 empty] | upper | lower | avg
mass of HFO in 1 kg fuel | kg | 0.31879 | [5 empty] | installation cost rate | 20 | 60 | 40 | €/kWfuel
mass of waste in 1kg fuel | kg | 0.68121 | [5 empty] | installation cost | 22500000 | 67500000 | 45000000 |  | 2326461.8862
PM
| HFO(%) | mixed-waste (%) | HFO (g) | mixed-waste(g) | Total mass in fuel (g/kgmix) |  |  | installation cost rate | 15 | 25 | avg
C | 87.3 | 48.62 | 278.3054 | 331.2034 | 609.5087 |  |  | installation cost | 16875000 | 28125000 | 22500000 |  | 1163230.9431
H | 10.9 | 5.79 | 34.7483 | 39.4419 | 74.1903 |  |  | annual operation cost rate | 0.1 | 0.1 | 0.1 | €/Mwfuel
N | 0.5 | 2.39 | 1.594 | 16.2809 | 17.8748 |  |  | annual operation cost | 112500 | 112500 | 112500
O | 0 | 43.2 | 0 | 294.2819 | 294.2819 |  |  | Cost per year |  |  | 1275730.9431
S | 0.95 | 0 | 3.0285 | 0 | 3.0285
ash | 0.05 | 0.37 | 0.1594 | 2.5205 | 2.6799 | 8526.3158 | 63094.7368 | 71621.0526
moisture content | 0.14 | 0 | 0.44631 | 0 | 0.44631
nitrogen in air (than oxygen) | 3.77
𝜆 | 1.1
| (in g) | M, g/mol | n, mol | O2 need,mol | CO2, mol | SO2,mol | H2O,mol | N2,mol
C | 609.5087 | 12 | 50.7924 | 50.7924 | 50.7924
H2 | 74.1903 | 2 | 37.0951 | 18.5476 |  |  | 37.0951
O2 | 294.2819 | 32 | 9.1963 | -9.1963
N2 | 17.8748 | 28 | 0.63839 |  |  |  |  | 0.63839
H2O | 0.44631 | 18 | 0.024795 |  |  |  | 0.024795
S | 3.0285 | 32 | 0.094641 | 0.094641 |  | 0.094641
ash | 2.6799
Total |  |  |  | 60.2383 | 50.7924 | 0.094641 | 37.1199 | 0.63839
from exercise
[5 empty] | n, mol | M, g/mol | m(g) | Vn,m3n/kmol | V, m3n
| oxygen need | 66.2621 |  | nO2 amount in CF | 6.0238 | 32 | 192.7625 | 22.39 | 0.13487
|  |  |  | nN2,mol anount in CF | 250.4466 | 28 | 7012.5045 | 22.4 | 5.61
|  |  |  | CO2,mol | 50.7924 | 44 | 2234.8653 | 22.26 | 1.1306
|  |  |  | SO2 mol | 0.094641 | 64 | 6.057 | 21.29 | 0.0020149
|  |  |  | H20, mol | 37.1199 | 18 | 668.1587 | 22.4 | 0.83149
[8 empty] | Dry comustion fumes | 6.8775
PM emissions calculation
[7 empty] | ash to bottom (%) | 70
[7 empty] | ash drifiting to combustion fumes(%) | 30
[6 empty] | mass of PM fumes(g/m3n) | 0.1169
[6 empty] | mass of PM | 0.80396
[6 empty] | mPM annually | 201254653.8761 | gPM/a | 201.2547 | tPM/a
| NOx emission calculation | [5 empty] | SO2 emission calculation |  | S+O2=SO2
| M for NO | 30 | nitrogen in fuel reacts to NOx (%) |  | 10 |  |  | M of S | 32
| M for NO2 | 46 | NO(%) | 95 |  |  |  | M of SO2 | 64
| M for O | 16 | NO2(%) | 5
| M for N | 14 |  |  |  |  | mSO2/mS | 2
| N2+O2=2NO | [5 empty] | mSO2 | 6.057 | gSO2/kgmix
| mNO/mN2 | 2.1429 |  |  |  |  | mSO2 fumes | 0.8807 | gSO2/m3n
| mNO | 3.8303 |  |  |  |  | mSO2 annually | 1516256157.6355 | g/a | 1516.2562 | tSO2/a
| mNO annually | 958841512.6486 | gNO/a | 958.8415 | tNO/a
NO+1/2O2=NO2
| mNO2/mNO | 1.5333
| mNO2 | 5.8732 |  |  |  |  | Carbon dioxide calculation |  | C+O2=CO2
| mNO2 annually | 1470223652.7279 | gNO2/a | 1470.2237 | tNO2/a |  | M for C | 12
| mNO2 fumes (gNO/m3n) |  | 0.85396 |  |  |  | M for CO2 | 44
| mNO fumes |  | 0.55693 |  |  |  | mCO2/mC | 3.6667
[7 empty] | mCO2 | 2234.8653 | g/kgmix
[7 empty] | mCO2 fumes | 324.9517 | g/m3n
[7 empty] | mCO2 annually | 559452208452.165 | g/a | 559452.2085 | tCO2/a
Note on G36: Pallav: ash from HFO
Note on H36: Pallav ash from sawdust
Note on I36: Pallav: total mass of ash